## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8420 | 6375 | 6582 | 1750 | 1838 | 21.54% | 21.83%
AC-2 | SERVING | 4375 | 4466 | 3300 | 3335 | 1075 | 1131 | 24.57% | 25.32%
AC-3 | DINNING/ RR | 5250 | 5324 | 3975 | 3979 | 1275 | 1345 | 24.29% | 25.26%
AC-4 | BOH | 1750 | 1772 | 1325 | 1333 | 425 | 439 | 24.29% | 24.77%
EF-1 | HD1 | [10 empty] | 1913 | 2004
EF-2 | HD2&HD3 | [10 empty] | 1402 | 1435
EF-3 | RESTROOMS | [12 empty] | 300 | 305
EF-4 | EMPL RR
EF-5
TOTALS |  | 19500 | 19982 | 14975 | 15229 | 4525 | 4753 |  |  | 0 | 0 | 3315 | 3439 | 300 | 305
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4753 |  | FRONT |  | 0.0176 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3744 |  | SIDE |  | 0.0185 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 910 | 1009 |  | REAR |  | 0.0133 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.016467 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390