## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Reception/FOH | 1675 | 1590 | 1621 | 1170 | 54 | 347 | 3.224% | 21.82%
RTU-2 | Exam Rooms/ Hallways | 1910 | 1978 | 1760 | 1688 | 150 | 309 | 7.853% | 15.62%
RTU-3 | Pet Wards/ Surgery | 2025 | 2125 | 1875 | 1880 | 150 | 371 | 7.407% | 17.46%
ERV-1 | RTU1 |  |  |  |  | 580 | 584 | - | 100.7% |  |  |  |  | 580 | 555
ERV-2 | RTU2 |  |  |  |  | 680 | 658 | - | 96.76% |  |  |  |  | 680 | 658
ERV-3 | RTU3 |  |  |  |  | 1250 | 1253 | - | 100.2% |  |  |  |  | 1245 | 1152
EF-1 | ISO | [12 empty] | 146 | 81
EF-2 | Lobby Restroom | [12 empty] | 50 | 54
EF-3 | BOH Restroom | [12 empty] | 50 | 63
EF-4 | Utility Closet | [12 empty] | 50 | 104
EF-5 | Dog Ward | [12 empty] | 50 | 57
TOTALS |  | 5610 | 5693 | 5256 | 4738 | 2864 | 3522 |  |  | 0 | 0 | 0 | 0 | 2851 | 2724
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2864 | 3522 |  | FRONT |  | 0.009 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2851 | 2724 |  | SIDE |  | 0.017 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 13 | 798 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.011667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0