## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3600 | 3509 | 3250 | 3144 | 350 | 365 | 9.722% | 10.4%
RTU-2 | DINING | 3400 | 3406 | 2600 | 2617 | 800 | 789 | 23.53% | 23.17%
EF-1 | HOOD FAN | [10 empty] | 700 | 1065
EF-2 | RESTROOMS | [12 empty] | 250 | 269
TOTALS |  | 7000 | 6915 | 5850 | 5761 | 1150 | 1154 |  |  | 0 | 0 | 700 | 1065 | 250 | 269
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1150 | 1154 |  | FRONT |  | 0.012 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 950 | 1334 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 200 | -180 |  | REAR |  | N/A | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.008 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
When fan speed is reduced to 746CFM, building pressure is +.008. Pressure not recorded at 1046CFM, however the fan had to be left at this speed to prevent overamping and potential damage to the fan.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0