## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8302 | 6375 | 6479 | 1750 | 1823 | 21.54% | 21.96%
AC-2 | DRIVE-THRU | 1600 | 1589 | 1200 | 1202 | 400 | 387 | 25% | 24.35%
AC-3 | DINING | 6300 | 6335 | 4600 | 4648 | 1700 | 1687 | 26.98% | 26.63%
AC-4 | TEAM ROOM | 1750 | 1751 | 1375 | 1349 | 375 | 402 | 21.43% | 22.96%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1971
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1437
EF-3 | RESTROOM | [12 empty] | 300 | 320
TOTALS |  | 17775 | 17977 | 13550 | 13678 | 4225 | 4299 |  |  | 0 | 0 | 3315 | 3408 | 300 | 320
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4225 | 4299 |  | FRONT |  | 0.02 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3728 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 610 | 571 |  | REAR |  | 0.01 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390