## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | 17919 WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2023-02-06 | Store#: | 17919 | Address: | 1900 Cameron St Raleigh, NC
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1
RTU 2
RTU 3
RTU 4
RTU 5
RTU 6
RTU 7
EH
SPLIT SYSTEM DATA
CU 1 | - | 2016 | - | York | PC120C00A4JAB4A | N1G6825113 | Normal wear and tear. Line set 1in and 1.5in |  | 10 | - | - | - | - | N | 460 | 485 | 3 | N | - | 30.75X55
CU 2 | Stockroom / Mgrs Office | 2016 | Reuse Heat Pump R-410A Condensing Unit | York | PC090C00A4JAB4A | N1G6793802 |  |  | 7.5 | - | - | - | - | N | 460 | 488 | 3 | N | - | 30.75X55
CU 3 | - | 2016 | - | York | PC120C00A4JAB4A | N1G6825114 | Normal wear and tear. Line set 1in and 1.5in |  | 10 | - | - | - | - | N | 460 | 485 | 3 | N | - | 30.75X55
CU 4 | - | 2016 | - | York | PC120C00A4JAB4A | N1G6825115 | Normal wear and tear. Line set 1in and 1.5in |  | 10 | - | - | - | - | N | 460 | 486 | 3 | N | - | 30.75X55
CU 5 | - | 2016 | - | York | YHJD30S44S4A | W1B6359159 | Normal wear and tear. Line set 1/4in and 3/4in |  | 2.5 | - | - | - | - | N | 208 | 212 | 3 | N | - | 34x34
CU 6 | - | 2016 | - | York | PC180C00A4GAB4A | N1G6813992 | Normal wear and tear. Line set 1in and 1.75in |  | 15 | - | - | - | - | N | 460 | 488 | 3 | N | - | 58x63
AHU 1 | Sales | 2016 | - | York | NC120C00C6AAA3 | N1G6829091 | Normal wear and tear. |  | 10 | Elec | 36KW | Duct | Return | Bldg | 460 | 486 | 3 | N | - | 30x56
AHU 2 | Stockroom / Mgrs Office | 2016 | FY24 ERF Received | York | NC090C00B6AAA2 | N1G6792120 | New York Production Equivalent to existing York NC090C00B6AAA2 Heat Pump Air Handler, 460/3/60, 1.5 HP Blower Motor. Reuse existing Heat Pump Condensing Unit, Mixing Box and Electric Heat Section. Normal wear and tear |  | 7.5 | Elec | 26KW | Duct | Return | Bldg | 460 | 485 | 3 | N | - | 30x56
AHU 3 | Stockroom | 2016 | - | York | NC120C00C6AAA3 | N1G6805001 | Normal wear and tear |  | 10 | Elec | 36KW | Duct | Return | Bldg | 460 | 488 | 3 | N | - | 30x56
AHU 4 | Sales | 2016 | - | York | NC120C00C6AAA3 | N1G6829092 | Normal wear and tear |  | 10 | Elec | 36KW | Duct | Return | Bldg | 460 | 487 | 3 | N | - | 30x56
AHU 5 | Pharmacy | 2016 | - | York | AHE30B3XH21B | W1F6680679 | Normal wear and tear |  | 2.5 | Elec | 7.2 | Duct | Return | N | 208 | 210 | 3 | N | - | 22X46
AHU 6 | Cosmetics/ Sales | 2016 | - | York | NC180C00E5AAA2 | N1G6793728 | Normal wear and tear |  | 15 | Elec | 50KW | Duct | Return | N | 460 | 487 | 3 | N | - | 33X74.5
VENTILATION DATA
ERV 1
ERV 2
EF 1 | Mens | - | Inline | No Tag | No Tag | No Tag | Unit is operational. |  | - | - | - | - | - | - | 115 | - | 1
EF 2 | Womens | - | Inline | No Tag | No Tag | No Tag |  |  | - | - | - | - | - | - | 115 | - | 1
EF 3
EF 4
EF 5
EF 6
EF 7
REFRIGERATION DATA
Roof mounted condenser | Cooler | - | Roof Mounted | Heat Craft | MOH008X62C | T16J12851 | 3/8 and 7/8 |  | - | - | - | - | - | - | 208 | 211 | 3 | N | 31x133 | 23.75x28.25
Roof mounted condenser | Cooler | - | Roof Mounted | Heat Craft | MOH008X62C | T16H25939 | 3/8 and 7/8 |  | - | - | - | - | - | - | 208 | 210 | 3 | N | 31X133 | 23.75X28.25
Roof mounted condenser | Freezer | - | Roof Mounted | Heat Craft | MOH025L63C | T16H26586 | 3/8 and 7/8 |  | - | - | - | - | - | - | 208 | 212 |  | N | 31X133 | 28.25X37.75
Roof mounted condenser
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | N | [5 empty] | AHU 1 | Breaker | Square D | HJ060 | 60 | 6 | 1.25
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) | N |  | Provid partner name |  |  |  | AHU 2 | Breaker | Square D | HJ060 | 60 | 6 | 1.25
If Partner Tenant Exists do they have full height walls? (Y/N) | - |  | Full height walls are defined as walls up to ceiling. |  |  |  | AHU 3 | Breaker | Square D | HJ060 | 60 | 6 | 1.25
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | N |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | AHU 4 | Breaker | Square D | HJ060 | 30 | 6 | 1.25
Tenant Space (Y/N): | N |  | Tenant Name (VMD/Kroger/LabCorp, etc.): |  |  |  | AHU 5 | Breaker | Square D | FH16050B | 50 | 6 | 1.25
Photo Lab (Y/N): | Y |  | Dry/Wet Lab: Dry |  |  |  | AHU 6 | Breaker | Square D | HJ150 | 150 | 6 | 1.25
Roof Condition (Good/Fair/Poor): | Good
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized |  | If "Other" Specify Type:
Unit Hail Damage (Y/N): | N
Store within 20 Miles of Ocean? (Y/N): | N
Existing EMS (Y/N): | Y |  | EMS Type(FSG/Gridpoint):
Fire Alarm Panel Operational (Y/N): | Y |  | Panel Model#: Uni Code System 10
Photo of Fire Alarm Panel Taken (Y/N): | Y
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | Remote
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: Reach In
Cooler: Reach In
Self-Contained Refrigeration ONLY Door Count: | Freezer: 5
Cooler: 20
Obvious Visual Damage to MDP (Y/N): | N |  | Explain Visual Damage:
Notes for Installer: | Roof access thru Crunch Fitness.
Original Curb Dimensional Data
RTU# | AHU 1 | AHU 2 | AHU 3 | AHU 4 | AHU 5 | AHU 6 | - | -
Curb Type
A (Length) | 56 | 56 | 56 | 56 | 46 | 74.5
B (Width) | 30 | 30 | 30 | 30 | 22 | 33
E | 23.5X25.25 Supply | 23.5X25.25 Supply | 23.5X25.25 Supply | 23.5X25.25 Supply | 15x18 Supply | 24x27 Supply
F | 21.5x54 Return | 21.5x54 Return | 21.5x54 Return | 21.5x54 Return | 17x22 Return | 21.5x54 Return
G
H
I
J
K
L
M
N
O