## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8541 | 6500 | 6485 | 2000 | 2056 | 23.53% | 24.07%
AC-2 | FOH | 1790 | 1820 | 1290 | 1339 | 500 | 481 | 27.93% | 26.43%
AC-3 | MEAL FULFILLMENT AREA | 2000 | 1954 | 1440 | 1387 | 560 | 567 | 28% | 29.02%
AC-4 | DINING | 4000 | 3970 | 2940 | 2939 | 1060 | 1031 | 26.5% | 25.97%
AC-5 | PLAY AREA | 1750 | 1677 | 1450 | 1365 | 300 | 312 | 17.14% | 18.6%
EF-1 | KITCHEN HD 1 | [10 empty] | 1913 | 1932
EF-2 | KITCHEN HD 2&3 | [10 empty] | 1402 | 1464
EF-3 | RESTROOMS | [12 empty] | 300 | 289
TOTALS |  | 18040 | 17962 | 13620 | 13515 | 4420 | 4447 |  |  | 0 | 0 | 3315 | 3396 | 300 | 289
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4420 | 4447 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3685 |  | SIDE |  | 0.02 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 805 | 762 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.010667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390