## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 2545 | 2250 | 1802 | 750 | 743 | 25% | 29.19%
RTU-2 | KITCHEN | 4500 | 4002 | 2750 | 2237 | 1750 | 1765 | 38.89% | 44.1%
KEF-1 | KITCHEN HD | [10 empty] | 1188 | 1154
KEF-2 | KITCHEN HD | [10 empty] | 860 | 861
EF-3 | RESTROOMS | [12 empty] | 200 | 196
TOTALS |  | 7500 | 6547 | 5000 | 4039 | 2500 | 2508 |  |  | 0 | 0 | 2048 | 2015 | 200 | 196
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2500 | 2508 |  | FRONT |  | -0.01 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2248 | 2211 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 252 | 297 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | -0.01 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1750 | 1765
TOTAL KITCHEN EXHAUST |  | 2048 | 2015
NET AIRFLOW |  | -298 | -250
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0