## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 7897 | 6500 | 5923 | 2000 | 1974 | 23.53% | 25%
AC-2 | SIDE DINING | 3150 | 2884 | 2325 | 2101 | 825 | 783 | 26.19% | 27.15%
AC-3 | MAIN DINING | 4000 | 4006 | 3000 | 3057 | 1000 | 949 | 25% | 23.69%
AC-4 | MAIN DINING | 2750 | 2912 | 2150 | 2302 | 600 | 610 | 21.82% | 20.95%
AC-5 | PLAY AREA | 2000 | 2026 | 1700 | 2026 | 300 | 0 | 15% | 0%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1833
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1296
EF-3 | RESTROOM | [12 empty] | 575 | 0
TOTALS |  | 20400 | 19725 | 15675 | 15409 | 4725 | 4316 |  |  | 0 | 0 | 3314 | 3129 | 575 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4725 | 4316 |  | FRONT |  | 0.0045 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3889 | 3129 |  | SIDE |  | 0.0043 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 836 | 1187 |  | REAR |  | 0.0034 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0040667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390