## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-A | DINING | 2000 | 2103 | 1550 | 1695 | 450 | 408 | 22.5% | 19.4%
RTU-A | KITCHEN | 2000 | 1801 | 1550 | 1395 | 450 | 406 | 22.5% | 22.54%
RTU-E2 | DINING | 1900 | 2060 | 1450 | 1619 | 450 | 441 | 23.68% | 21.41%
RTU-E3 | DINING | 2000 | 1802 | 2000 | 1802 |  | 0 | 0% | 0%
RTU-E4 | SERVING | 2000 | 2196 | 1550 | 1703 | 450 | 493 | 22.5% | 22.45%
EF-1 | HD1 | [10 empty] | 5300 | 4705
MAU | HOOD | [13 empty] | 2452
TOTALS |  | 9900 | 9962 | 8100 | 8214 | 1800 | 1748 |  |  | 0 | 0 | 5300 | 4705 | 0 | 2452
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1800 | 1748 |  | FRONT | [10 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 5300 | 7157 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | -3500 | -5409 |  | REAR |  | 0.026 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.026 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES: | EF2 FAN IS NOT RUNNING
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0