## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6000 | 5796 | 4175 | 3950 | 1825 | 1846 | 30.42% | 31.85%
RTU-2 | KITCHEN | 6225 | 6001 | 4450 | 4221 | 1775 | 1780 | 28.51% | 29.66%
PRV-1 | RESTROOM | [12 empty] | 300 | 294
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1469
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1538
EF-1A(X2) | EMP.RR/MOP | [12 empty] | 150 | 145
TOTALS |  | 12225 | 11797 | 8625 | 8171 | 3600 | 3626 |  |  | 0 | 0 | 3000 | 3007 | 450 | 439
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3600 | 3626 |  | FRONT |  | 0.0035 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3446 |  | SIDE |  | 0.0016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 150 | 180 |  | REAR |  | 0.0023 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0024667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
OA taken under windy conditions
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0