## SD1-11,12
ROUND DUCT TRAVERSE FORM
PROJECT: |  | Brightview Senior Living |  |  | SYSTEM: | DOAS 1
LOCATION - ZONE: |  | Attic |  |  | SERVICE: | Supply Register 11/12
ALTITUDE: |  |  |  | DENSITY: | FACTOR:
DUCT |  |  | REQUIRED |  | ACTUAL
S.P.: | 0.14" |  | SCFM: |  | SCFM:
SIZE: | 6" |  | FPM: | 450 | FPM: | 498
AREA: | 0.35Ft^2 |  | CFM: | 90 | CFM: | 100
TEMP:
TEST DATE: |  |  | REMARKS:
2025-09-18
READINGS BY:
Tyler Y
481
473
489
476
633
435

## SD1-10
ROUND DUCT TRAVERSE FORM
PROJECT: |  | Brightview Senior Living |  |  | SYSTEM: | DOAS 1
LOCATION - ZONE: |  | Attic |  |  | SERVICE: | Supply Register 10
ALTITUDE: |  |  |  | DENSITY: | FACTOR:
DUCT |  |  | REQUIRED |  | ACTUAL
S.P.: | 0.14" |  | SCFM: |  | SCFM:
SIZE: | 6" |  | FPM: | 326 | FPM: | 311
AREA: | 0.35Ft^2 |  | CFM: | 65 | CFM: | 61
TEMP:
TEST DATE: |  |  | REMARKS:
2025-09-18
READINGS BY:
Tyler Y
201
365
340
299
331
331

## RD1-7
SQUARE DUCT TRAVERSE FORM
PROJECT | Brightview Senior Living | [5 empty] | SYSTEM | DOAS-1
LOCATION | Eatontown, NJ | [5 empty] | SERVICE | Exhaust Register 7
ALTITUDE | 4 |  | DENSITY | 4 |  |  | FACTOR | 4
DUCT |  |  |  |  | REQUIRED |  |  |  | ACTUAL
S.P. | 0.013" |  | TEMP | 4 | SCFM | 4 |  |  | SCFM | 4
SIZE | 11"X6" |  |  |  | FPM | 360 |  |  | FPM | 207
AREA | 0.458Ft^2 |  |  |  | CFM | 165 |  |  | CFM | 95
DISTANCE
FROM | POSITION | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
BOTTOM
1.5" | 1 | 1: 283; 2: 156; 3: 182
4.5" | 2 | 1: 226; 2: 202; 3: 195
3
4
5
6
7
8
9
10
11
12
13
DISTANCE FROM |  | 1: 1.83"; 2: 5.5"; 3: 9.15"
DUCT EDGE
VELOCITY
SUB - TOTALS
REMARKS:
[1] TRAVERSE TAKEN FROM ATTIC, NO SIGNS OF LEAKAGE ALONG DUCTWORK.

## RD1-8
ROUND DUCT TRAVERSE FORM
PROJECT: |  | Brightview Senior Living |  |  | SYSTEM: | DOAS-1
LOCATION - ZONE: |  | Attic |  |  | SERVICE: | Exhaust Register 7
ALTITUDE: |  |  |  | DENSITY: | FACTOR:
DUCT |  |  | REQUIRED |  | ACTUAL
S.P.: | 0.02" |  | SCFM: |  | SCFM:
SIZE: | 8" |  | FPM: | 229 | FPM: | 223
AREA: | 0.35Ft^2 |  | CFM: | 80 | CFM: | 78
TEMP:
TEST DATE: |  |  | REMARKS:
2025-09-18
READINGS BY:
Tyler Y
213
242
222
226
171
236
249
235

## RD1-12
ROUND DUCT TRAVERSE FORM
PROJECT: |  | Brightview Senior Living |  |  | SYSTEM: | DOAS 1
LOCATION - ZONE: |  | Attic |  |  | SERVICE: | Exhaust Register 10
ALTITUDE: |  |  |  | DENSITY: | FACTOR:
DUCT |  |  | REQUIRED |  | ACTUAL
S.P.: | 0.008" |  | SCFM: |  | SCFM:
SIZE: | 8" |  | FPM: | 214 | FPM: | 170
AREA: | 0.35Ft^2 |  | CFM: | 75 | CFM: | 59
TEMP:
TEST DATE: |  |  | REMARKS:
2025-09-18
READINGS BY:
Tyler Y
168
211
185
206
203
165
43
181

## Exhaust D1(5-11) Total
SQUARE DUCT TRAVERSE FORM
PROJECT | Brightview Senior Living | [5 empty] | SYSTEM | DOAS-1
LOCATION | Hallway-diffuser access | [5 empty] | SERVICE | Exhaust Grilles 5-11
ALTITUDE | 4 |  | DENSITY | 4 |  |  | FACTOR | 4
DUCT |  |  |  |  | REQUIRED |  |  |  | ACTUAL
S.P. | 0.07" |  | TEMP | 4 | SCFM | 4 |  |  | SCFM | 4
SIZE | 14"x12" |  |  |  | FPM | 711 |  |  | FPM | 539
AREA | 1.167Ft^2 |  |  |  | CFM | 830 |  |  | CFM | 629
DISTANCE
FROM | POSITION | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
BOTTOM
2" | 1 | 1: 579; 2: 600; 3: 589; 4: 560
6" | 2 | 1: 612; 2: 603; 3: 626; 4: 420
10" | 3 | 1: 616; 2: 620; 3: 441; 4: 206
4
5
6
7
8
9
10
11
12
13
DISTANCE FROM |  | 1: 1.75"; 2: 5.25"; 3: 8.75"; 4: 12.5"
DUCT EDGE
VELOCITY
SUB - TOTALS
REMARKS:
Traverse total of the duct serving 6 of the exhaust grilles is 630 CFM. Total flow hoods readings sum of 472CFM with the low flow hood