## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8432 | 6375 | 6738 | 1750 | 1694 | 21.54% | 20.09%
AC-2 | FOH | 4375 | 4392 | 3300 | 3300 | 1075 | 1092 | 24.57% | 24.86%
AC-3 | DINING | 5250 | 5264 | 3975 | 3916 | 1275 | 1348 | 24.29% | 25.61%
AC-4 | BOH | 1750 | 1771 | 1325 | 1333 | 425 | 438 | 24.29% | 24.73%
EF-1 | KITCHEN HD 1 | [10 empty] | 1913 | 1846
EF-2 | KITCHEN HD 2&3 | [10 empty] | 1402 | 1451
EF-3 | RESTROOMS | [12 empty] | 300 | 290
TOTALS |  | 19500 | 19859 | 14975 | 15287 | 4525 | 4572 |  |  | 0 | 0 | 3315 | 3297 | 300 | 290
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4572 |  | FRONT |  | 0.008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 3587 |  | SIDE |  | 0.02 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 910 | 985 |  | REAR |  | 0.008 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Bulding pressure taken with some missing ceiling tiles and drive through door not sealed.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390