## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Dining | 6750 | 6614 | 4795 | 4531 | 1955 | 2083 | 28.96% | 31.49%
RTU-2 | Kitchen | 6150 | 5896 | 4655 | 4334 | 1495 | 1562 | 24.31% | 26.49%
PRV-1 | Restrooms | [12 empty] | 375 | 388
PRV-2 | HD1 | [10 empty] | 1500 | 1523
PRV-3 | HD2 | [10 empty] | 1500 | 1587
EF-1A | Mop Room | [12 empty] | 75 | 80
TOTALS |  | 12900 | 12510 | 9450 | 8865 | 3450 | 3645 |  |  | 0 | 0 | 3000 | 3110 | 450 | 468
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3645 |  | FRONT |  | 0.006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3578 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 67 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0