## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3200 | 3195 | 1940 | 1923 | 1260 | 1272 | 39.38% | 39.81%
RTU-2 | KITCHEN | 4050 | 3992 | 3740 | 3661 | 310 | 331 | 7.654% | 8.292%
FCU-1 | OFFICE |  |  |  |  | 40 | 41 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 1800 | 1717
KEF-1 | HOOD 1 | [10 empty] | 1714 | 1692
KEF-2 | HOOD 2 | [10 empty] | 733 | 717
EF-1 | RESTROOMS | [12 empty] | 450 | 447
TOTALS |  | 7250 | 7187 | 5680 | 5584 | 1610 | 1644 |  |  | 1800 | 1717 | 2447 | 2409 | 450 | 447
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3410 | 3361 |  | FRONT |  | 0.0021 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2897 | 2856 |  | SIDE |  | 0.0027 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 513 | 505 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0019333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2110
TOTAL KITCHEN EXHAUST |  | 2447
NET AIRFLOW |  | -337 | 0
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0