## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 5250-6000 | 5359 |  |  |  | NOTES
RTU-2 |  | 2650-3050 | 2179 |  |  |  | NOTES
MUA-1 | [10 empty] | 3488
KEF-1 | [12 empty] | 1978
KEF-2 | [12 empty] | 2048
EF-3 | [14 empty] | 0
TOTALS |  | 0 | 7538 | 0 | 0 | 0 | 0 |  |  | 0 | 3488 | 0 | 4026 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN:
TOTAL OA |  | 0 | 3488 |  | FRONT |  | 0.007 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 0 | 4026 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW:
NET AIRFLOW |  | 0 |  |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0065 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Unable to record an accurate outside air reading at the RTUs due to winds. Economizers cracked and building pressure measured to be slightly positive.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0