## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3475 | 3422 | 450 | 247 | 3025 | 3175 | 87.05% | 92.78%
EF-1 | KITCHEN HOOD | [10 empty] | 2850 | 2891
EF-2 | RESTROOM | [12 empty] | 75 | 82
TOTALS |  | 3475 | 3422 | 450 | 247 | 3025 | 3175 |  |  | 0 | 0 | 2850 | 2891 | 75 | 82
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3025 | 3175 |  | FRONT |  | -0.0014 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2925 | 2973 |  | SIDE |  | 0.0016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 202 |  | REAR |  | N/A | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0001 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X20 | [9 empty] | 2850 |  | -2850