## Report Sheet
STORE #: | 3500 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | PAINESVILLE, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-06 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12D2B5HAA2A2 | N1H9215731 | RTU-1 | KITCHEN | 500 | 337 | 0 | 0 |  | 1759 | 1759 | 723 | 723 | 2 | 213.3 | 213.3 | 3 | 6.6 | 5 | 5 | 1.7828 | 1.7828 | 0%
YORK | ZJ090N18D2B5HAA2A2 | N1K9286791 | RTU-2 | DINING | 1000 | 0 | 1000 | 0 |  | 1732 | 1732 | 1013 | 1013 | 3 | 211.3 | 2113 | 3 | 9.4 | 7.39 | 7.39 | 2.6103 | 26.1027 | 900%
CAPTIVE AIRE | A1-D.250-G10 | 3925315 | MUA-1 | HOOD 1 | 1950 | 1756 | 1700 | 1756 | No | 1784 | 1784 | 848 | 848 | 2 | 212.5 | 212.5 | 3 | 5.38 | 2.48 | 2.48 | 0.88095 | 0.88095 | 0%
CAPTIVE AIRE | NCA24HPFA | 3925315 | EF-1 | HOOD 1 | 3200 | 2566 | 2450 | 2566 | No | 1773 | 1773 | 780 | 780 | 2 | 212.2 | 212.2 | 3 | 5.38 | 3.11 | 3.11 | 1.1032 | 1.1032 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2093 | 2700 | 1756 |  | FRONT DOOR |  | -0.0049 |  |  | INITIAL | 6.3772 | 2093
|  |  | TOTAL EXHAUST |  | 3350 | 2716 | 2600 | 2716 |  | BACK DOOR |  | -0.0059 |  |  | FINAL | 29.8696 | 4322
|  |  | NET AIRFLOW |  | 100 | -623 | 100 | -960 |  | AVERAGE |  | -0.0054 |  |  | ∆ | -23.4924 | -2229
Issue List
Unit # | Description
Select from drop down list
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
RTU-2 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
,./

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.