## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3041 | 1900 | 1904 | 1100 | 1137 | 36.67% | 37.39%
RTU-2 | KITCHEN | 5000 | 4997 | 3600 | 3521 | 1400 | 1476 | 28% | 29.54%
EF-1 | KITCHEN HD | [10 empty] | 1188 | 1164
EF-2 | KITCHEN HD | [10 empty] | 875 | 886
EF-3 | RESTROOM | [12 empty] | 200 | 193
TOTALS |  | 8000 | 8038 | 5500 | 5425 | 2500 | 2613 |  |  | 0 | 0 | 2063 | 2050 | 200 | 193
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2500 | 2613 |  | FRONT |  | 0.0042 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2263 | 2243 |  | SIDE |  | 0.0032 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 237 | 370 |  | REAR |  | 0.0022 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0032 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1400 | 1476
TOTAL KITCHEN EXHAUST |  | 2063 | 2050
NET AIRFLOW |  | -663 | -574
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0